# Vibration Sensor (iSN-713) to Laptop / Backend – Complete Setup Guide

Purpose: This document explains, step by step, how vibration data was successfully obtained from the iSN-713 Modbus RTU vibration sensor using a TGW-718 Modbus TCP gateway, verified via Modbus tools, and finally made available to a backend system.

Note: Code snippets are intentionally skipped. Space is left for screenshots (SS) where indicated.

## 1. Hardware Used

- iSN-713 MRTU Vibration Sensor

- TGW-718 Modbus RTU → Modbus TCP Gateway

- 12V DC Power Adapter (for TGW-718)

- RS-485 Cable (Sensor → Gateway)

- Ethernet Cable (Gateway → Network)

- LAN to USB-C Converter (Laptop without Ethernet port)

- Laptop / PC

## 2. Physical Connections

### 2.1 Power Connections

- TGW-718 powered using 12V DC adapter

- iSN-713 powered as per datasheet (via RS-485 / external supply)

### 2.2 RS-485 Wiring (Sensor → Gateway)

| iSN-713 | TGW-718 |
| --- | --- |
| D+ | Data+ |
| D- | Data- |

- Ensure correct polarity (D+ to D+, D- to D-)

- Keep cable length short and twisted pair preferred

### 2.3 Ethernet Connection

- TGW-718 Ethernet port → LAN cable

- LAN cable → USB-to-Ethernet adapter → Laptop

## 3. TGW-718 Initial Configuration

### 3.1 RUN / INIT Switch

- Set switch to INIT for reset / IP recovery

- Power ON → wait 10 seconds

- Power OFF → set switch to RUN

- Power ON again

This restores default network and login settings.

### 3.2 Network Settings

- Default IP of TGW-718: 192.168.1.100

- Laptop Ethernet IP set manually, e.g.:

  - IP: 192.168.1.10

  - Subnet: 255.255.255.0

Test connectivity: - Ping 192.168.1.100

## 4. Accessing TGW-718 Web Interface

- Open browser → http://192.168.1.100

- Login page may not visibly change after submit

- Default password used: admin

## 5. Serial (RS-485) Configuration in TGW-718

### 5.1 Port Settings

Configured according to iSN-713 quick start guide:

- Baud Rate: 9600

- Data Bits: 8

- Parity: None (disabled / fixed by device)

- Stop Bits: 1

- Mode: Modbus RTU Master

⚠️ Parity option may be disabled – this is normal for TGW-718 firmware.

### 5.2 Modbus Mapping Mode

- TGW-718 configured as:

  - RTU (sensor side) → TCP (network side)

- Gateway acts as Modbus TCP slave on port 502

## 6. Understanding iSN-713 Modbus Data

The iSN-713 does not provide X/Y/Z axis data.

Instead, it provides scalar vibration metrics via Input Registers (3xxxx).

### 6.1 Registers Used

| Register | Meaning |
| --- | --- |
| 30023 | Acceleration RMS |
| 30024 | Acceleration Max |
| 30025 | Acceleration Peak-to-Peak |
| 30026 | Crest Factor |
| 30027 | Velocity RMS |

### 6.2 Scaling Rules

- Acceleration values → mg (milligravity)

- Crest factor → value × 0.01

- Velocity RMS → value × 0.01 mm/s

Example raw data:

[ 10, 58, 56, 54, 38 ]

Converted values: - Accel RMS: 10 mg - Accel Max: 58 mg - Accel P-P: 56 mg - Crest Factor: 0.54 - Velocity RMS: 0.38 mm/s

## 7. Verifying Data Using Modbus Tool

Before backend integration, data was verified using:

- Modbus Poll / Modbus Doctor

- Connection type: Modbus TCP

- IP: 192.168.1.100

- Port: 502

- Slave ID: 1

- Function Code: 04 – Read Input Registers

- Start address: 30023

- Length: 5

⚠️ Only one Modbus master should be connected at a time.

## 8. Backend Integration Overview (High Level)

- Backend connects to TGW-718 using Modbus TCP

- Polls input registers periodically (e.g., every 1 second)

- Converts raw register values into engineering units

- Emits live data via WebSocket

- Stores structured data into MongoDB

## 9. Final Data Model (Conceptual)

Each vibration sample consists of:

- Timestamp

- Acceleration (RMS, Max, Peak-to-Peak)

- Velocity RMS

- Crest Factor

- Raw register values (for debugging & traceability)

This model supports: - Live dashboards - Historical analysis - Alarm thresholds - Predictive maintenance

## 10. Result

✔ Stable Modbus TCP communication ✔ Real-time vibration data available ✔ Data validated against Modbus tools ✔ Ready for frontend visualization and alerts

## 11. Next Possible Enhancements

- ISO 10816 vibration severity limits

- Alarm & notification system

- FFT spectrum analysis (if supported)

- Data downsampling & aggregation

- Cloud deployment

https://chatgpt.com/share/698c688d-4ea8-800f-9c7a-491194c8cbcd

MQTT